## Introduction
Introduction
Within Scottish and Southern Electricity Networks (SSEN), we are looking to ascertain suppliers capable of providing LV phase balancing and power quality measuring devices, as further detailed in the specification sheets. This is initially to support an innovation project.
The purpose of this Request for Information (RFI) is for the market to provide information only. This process of engagement is not a pre-qualification, tender nor a guarantee of any future tender opportunities. This process also does not guarantee any agreements, contracts or delivery of the required goods.
RFI Contact Point
Susan Beveridge, Junior Category Manager for Future Networks
susan.e.beveridge@sse.com
Response Timeline
Please submit responses to Susan Beveridge by email by close of business Friday 2nd December 2022
Requirement
If this is something that your company may be able to offer to SSEN, please respond to the questions listed below, and provide any additional supporting information that is relevant.
Question | Response
Company name
Company full address
Website address
Point of contact
Contact email address
Contact telephone number
Brief overview of company
LV Phase Balancing
Are you able to supply LV Phase Balancing devices in compliance with the required characteristics detailed in the specification?
If yes, can you please provide further details on the device you could offer (including spec sheets where applicable)?
If no, are you able to provide a device that while not compliant with the required characteristics would still address the problem? If you can, please provide further details (including spec sheets where applicable)?
Please provide any additional information you feel is relevant regarding the LV Phase Balancing devices that we are looking for.
Power Quality Measuring
Are you able to supply Power Quality Measuring devices in compliance with the required characteristics detailed in the specification?
If yes, can you please provide further details on the device you could offer (including spec sheets where applicable)?
If no, are you able to provide a device that while not compliant with the required characteristics would still address the problem? If you can, please provide further details (including spec sheets where applicable)?
Please provide any additional information you feel is relevant regarding the Power Quality Measuring devices that we are looking for.

## LV Phase Balancing Spec
LV Phase Balancing Spec Sheet
Problem
The transition to Net Zero will require significant electrification of low carbon technologies (LCTs) to be connected to the Low Voltage (LV) Network, such as Electric Vehicles (EV), Heat Pumps (HP) and Photovoltaic (PV). As LCTs are mainly single phase and inverter-based technology, they may have a negative impact on power quality (PQ) and balance on the network, which in turn impacts the efficiency of the system and ability to deliver required power to end customers.
Solution
We are seeking a solution to the unbalanced load and PQ problems described above. The solution should have the following characteristics:
· Device must work on 3 phase LV networks (230/400 VAC)
· Device must be able to balance the load between phases.
· Device must be able to be installed either in outdoor environments on poles or substations or in indoor distribution substations or as a street furniture.
· Device should have monitoring function of load conditions and rebalancing actions.
· Device should rebalance load automatically based on a set point or through manual control signals.
· Device must be TRL 8 or higher as we plan to do a trial installation on our network
· The rating of the device needs to be minimum of 22 kVA (minimum of 7.4 kVA per phase)
· Device should be low maintenance and life expectancy >5 years.
· Device could have active filter functionality to rectify harmonic distortion.
· Device could have voltage support and power factor correction functionality (reactive power capability).

## Power Quality Measuring Device
Power Quality Measuring Device Spec Sheet
Problem
The transition to Net Zero will require significant electrification of low carbon technologies (LCTs) to be connected to the Low Voltage (LV) Network, such as Electric Vehicles (EV), Heat Pumps (HP) and Photovoltaic (PV). As LCTs are mainly single phase and inverter-based technology, they may have a negative impact on power quality (PQ) and balance on the network, which in turn impacts the efficiency of the system and ability to deliver required power to end customers.
Solution
We are seeking a solution to the unbalanced load and PQ problems described above. The solution should have the following characteristics:
· Household PQM needs to have voltage measurement and at least one current measurement.
· Single phase able to measure frequency up-to 50th Harmonic (50 Hz system)
· Voltage measurement (230 VAC nominal (up to 280 VAC)
· Current measurement (minimum 32 Amps (preferably up to 100 Amps)
· Safe to install with CE certificate
· Easy to remove.